## Bus
This sheet summarizes the parameters for power flow analysis
Bus | Type | Vsp (pu) | theta (rad) | PGi (pu) | QGi (pu) | PLi (pu) | QLi (pu) | Qmin (pu) | Qmax (pu) | Area No. | AC or DC
1 | 1 | 1.06 | 0 | 0 | 0 | 0 | 0 | -999 | 999 | 1 | 1
2 | 2 | 1.045 | 0 | 0.4 | 0.424 | 0.217 | 0.127 | -999 | 999 | 1 | 1
3 | 3 | 1.01 | 0 | 0.6 | 0.234 | 0.942 | 0.19 | -999 | 999 | 1 | 1
4 | 3 | 1 | 0 | 0 | 0 | 0.478 | -0.039 | 0 | 0 | 1 | 1
5 | 3 | 1 | 0 | 0 | 0 | 0.076 | 0.016 | 0 | 0 | 1 | 1
6 | 2 | 1.07 | 0 | 0.5 | 0.122 | 0.112 | 0.075 | -999 | 999 | 1 | 1
7 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
8 | 3 | 1.09 | 0 | 0.3 | 0.174 | 0 | 0 | -999 | 999 | 1 | 1
9 | 3 | 1 | 0 | 0 | 0 | 0.495 | 0.166 | 0 | 0 | 1 | 1
10 | 3 | 1 | 0 | 0 | 0 | 0.09 | 0.058 | 0 | 0 | 1 | 1
11 | 3 | 1 | 0 | 0 | 0 | 0.235 | 0.018 | 0 | 0 | 1 | 1
12 | 3 | 1 | 0 | 0.3 | 0.074 | 0.261 | 0.016 | -999 | 999 | 1 | 1
13 | 3 | 1 | 0 | 0 | 0 | 0.535 | 0.058 | 0 | 0 | 1 | 1
14 | 3 | 1 | 0 | 0 | 0 | 0.349 | 0.05 | 0 | 0 | 1 | 1

## Apparatus
This sheet summarizes the apparatuses connected to buses.
%===============================
% 0000-0100: AC device
%===============================
| 0-9: Synchronous generator |  | 10-19: Grid-following inverter |  |  | 20-29: Grid-forming inverter |  |  | 30-39: Detailed Synchronous machine |  |  |  | 40-49: Cyprus Synchronous machine |  |  |  | 90: AC infinite bus (short circuit in small-signal) |  |  |  | 100: AC floating bus (open circuit)
|  |  | 10, 11, 17: |  |  | 20: VSG |  |  | 33: govenor
|  |  | 19: xx |  |  | 28: Old type |  |  | 35: AVR, PSS, GOV
18: simplified current loop
[16 empty] | EXCITER | [16 empty] | PSS
| SM | X | R | x_d | x'd | x''d | T'd | T''d | xq | x'q | x''q | T'q | T''q | H | D | input filter time constant T_R | voltage regulator gain K_A | voltage regulator time constant T_A | maximum voltage regulator output V_Rmax | minimum voltage regulator output V_Rmin | exciter constant K_E | exciter time constant T_E | E_1 | S(E_1) | E_2 | S(E_2) | stabilizer gain K_F | stabilizer time constant T_F | K_P | K_I | K_D | T_D | KPSS | TW | T11 | T12 | T21 | T22 | T31 | T32 | VSSmax | VSSmin
| GFM | wLf | Rf | wCf | wLc | Rc | Xov | Dw | fdroop | fvdq | fidq | Sbase
| GFL | V_dc | C_dc | wLf | R | f_v_dc | f_pll | f_i_dq | Sbase
1 | 35 | 0.199 | 0.0001 | 1.69 | 0.457 | 0.4 | 9.37 | 0.05 | 1.15 | 0.61538 | 0.4 | 1.5 | 0.035 | 31 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
2 | 35 | 0.295 | 0.01 | 2.62 | 0.436 | 0.35 | 5.69 | 0.05 | 2.58 | 0.58571 | 0.35 | 1.5 | 0.035 | 28.6 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
3 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 20 | 400 | 1
4 | SM: 100
5 | SM: 100
6 | 28 | 0.1 | 0.02 | 0.01 | 0.02 | 0.004 | 0.001 | 0.001 | 10 | 150 | 900 | 2
7 | SM: 100
8 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 20 | 420 | 1
9 | SM: 100
10 | SM: 100
11 | SM: 100
12 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 100 | 500 | 1
13 | SM: 100
14 | SM: 100

## NetworkLine_IEEE
This sheet summarizes the parameters for network line impedance in IEEE form.
Enable:
1
User data:
From bus | To bus | R (pu) | X (pu) | B (pu) | G (pu) | Turns Ratio (pu)
1 | 2 | 0.01938 | 0.05917 | 0.0528 | 0 | 1
1 | 5 | 0.05403 | 0.22304 | 0.0492 | 0 | 1
2 | 3 | 0.04699 | 0.19797 | 0.0438 | 0 | 1
2 | 4 | 0.05811 | 0.17632 | 0.034 | 0 | 1
2 | 5 | 0.05695 | 0.17388 | 0.0346 | 0 | 1
3 | 4 | 0.06701 | 0.17103 | 0.0128 | 0 | 1
4 | 5 | 0.01335 | 0.04211 | 0 | 0 | 1
4 | 7 | 0 | 0.20912 | 0 | 0 | 0.978
4 | 9 | 0 | 0.55618 | 0 | 0 | 0.969
5 | 6 | 0 | 0.25202 | 0 | 0 | 0.932
6 | 11 | 0.09498 | 0.1989 | 0 | 0 | 1
6 | 12 | 0.12291 | 0.25581 | 0 | 0 | 1
6 | 13 | 0.06615 | 0.13027 | 0 | 0 | 1
7 | 8 | 0 | 0.17615 | 0 | 0 | 1
7 | 9 | 0 | 0.11001 | 0 | 0 | 1
9 | 10 | 0.03181 | 0.0845 | 0 | 0 | 1
9 | 14 | 0.12711 | 0.27038 | 0 | 0 | 1
10 | 11 | 0.08205 | 0.19207 | 0 | 0 | 1
12 | 13 | 0.22092 | 0.19988 | 0 | 0 | 1
13 | 14 | 0.17093 | 0.34802 | 0 | 0 | 1
9 | 9 | inf | inf | 0.19 | 0 | 1

## NetworkLine
This sheet summarizes the parameters for network line impedance.
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio (pu)

## Basic
This sheet summarizes basic settings
Samping frequency (Hz) | 100000
Base frequency (Hz) | 60
Base power (VA) | 1
Base voltage (V) | 1

## Advance
This sheet summaries advanced settings.
Item | Value
Discretization method | 2
Linearization times | 1
Discretization damping flag | 1
Direct feedthrough | 0
Power flow algorithm | 2
Enable (create simulink model) | 0
Enable (plot pole map) | 1
Enable (plot admittance) | 1
Enable (print output) | 1
Enable (modal analysis) | 1